# JS Air Curtains Maxwell, Air Curtain Specification

- The Maxwell Air Curtain is a powerful industrial unit with “Coanda” effect double outlets to help achieve an increased air jet velocity. Designed for vertical or horizontal installation, it is constructed with a self-supporting galvanized steel casing.

- The Maxwell casing is finished with a structural epoxy-polyester paint finish, offered as standard in RAL 9016 with other classic RAL colours, or a brushed stainless steel finish, available on request.

- The unit is equipped with ‘AC’ Axial fans, powered by an external rotor motor and featuring low noise levels. They offer five selectable fan speeds and are equipped with built-in thermal protection.

- The Maxwell unit shall measure 511mm high by 660mm deep and can be supplied in various lengths ranging from 1.5m to 3.5m in 0.5m increments. Multiple units may be joined together through its multiple modules.

- The unit is suitable as standard for exposed, horizontal mounting above door, hung using M8 threaded drop rods. An optional base plate with floor fixing points shall be available, to allow vertical mounting to side of the doorway. Optional brackets may be specially ordered for overhead or wall mounting, including, wall ‘rail’ supports and suspension cables.

- The unit can be specified with ‘A’ type (low-energy air only, unheated or recirculating ambient air), or ‘P’ type (LPHW water coil).

- ‘P’ type water heated units offer either on/off, or proportional heating control, depending on valve type, with coil options for 60°C or 80°C flow. External solenoid valves shall also be available on request.

- The unit comes with anodised aluminium vanes shaped like air foils to minimise drag and noise. Each vane can be adjusted from 0 to 15º from the vertical to control the direction of airflow.

- The Maxwell is equipped as standard with an ‘Advanced Pro’ digital controller, featuring a 2.8” backlit LCD status screen, capacitive touch buttons, a tamperproof screen lock and a lacquered PCB for enhanced protection against moisture and dust. The package also includes a 7m, RJ11 control cable, door contact and a handheld infrared remote control.

- The Advanced Pro controller features an integrated temperature sensor, with semi-automatic ECO mode for setpoint regulation, with manual override for temperature and fan speed adjustment. ECO Mode settings can be configured based on door status, including door delay (0 to 95 sec), maximum speed and heating (open and closed), maintenance/filter intervals (0 to 92 weeks), temperature boost mode, and additional related functions.

- The controller features ‘Plug & Play’, auto configuration with a backlit LCD showing temperature, fan speed, heating, door status, alarm/error and unit off. It also includes three digital inputs for BMS/timer enable/disable, heat enable/disable, fire alarm disable, with manual safety reset.

- The optional ‘Clever Pro’ controller includes ‘Advance Pro’ features (excluding fire alarm input), plus a 7-day timer, and Modbus RTU compatibility with BMS, for remote control.

- The Maxwell air curtain is produced to ISO 9001 standards, fully run tested for reliability, with traceable documentation for quality, CE & UKCA certified and compliant with relevant regulations. BIM files can be provided upon request.

- The system is to be supplied by:

JS Air Curtains Limited 						www:	Maxwell Air Curtain

City Gates, 2-4 Southgate

Chichester

West Sussex								Tel:	+44 (0)333 038 4240

PO19 8DJ 								e-mail:	sales@jsaircurtains.com

United Kingdom 							Website:	www.jsaircurtains.com