JS Air Curtains Rotowind

Air Curtain Specification Summary

- The Air Curtain shall have a self-supporting casing made of galvanized plated steel, finished in structural epoxy-polyester RAL 9016 as standard. Other RAL colours or brushed stainless steel construction shall be available on request.

- The Air Curtain shall use low noise centrifugal double inlet fans driven by an external rotor motor with built in thermal protection.

- The Air Curtain shall be available as standard in a choice of 2 different fan powers to suit different mounting heights and environments using AC type fans.

- The Air Curtain shall also be available with an option of EC fans for energy saving.

- The fans shall be capable of 5 speed selections.

- The Air Curtain shall be available in a choice of sizes nominally from 1.0m to 2.5m in 0.5m increments. Very large doors shall be covered with two units in tandem.

- The Air Curtain shall be supplied with custom made plenum / ducting to suit the curvature of the door. A plenum cover shall be available and is recommended for most installations.

- The unit shall be specially designed to suit revolving and sliding circular doors. Two general layouts shall be available “on top” and “false ceiling” mounting.

- The inlet grille shall be perforated with filter function. For servicing, in normal environments, the grille only has to be periodically wiped or vacuumed.

- The Air Curtain shall be available with a choice of water, electric heating or ambient unheated.

- Water heated units will be available as standard with a choice of 2 coil types suitable for 80 or 60C flow. Special coils for use with “low grade” water will also be available by request.

- Electrically heated units will use 400V 3 phase, shielded elements with three heat settings with power contactors included.

- The Air Curtain will use anodised aluminium blow-out vanes, airfoil shaped.

- The Air Curtain shall include as standard a manual controller, 7m of telephonic cable with RJ45 (Plug & Play) connectors and a hand held infra-red remote.

- The manual controller shall be capable of BMS/PLC/Timer etc. enable and disable by a suitable volt free contact.

- Electrically heated units shall be capable of accepting a thermostat connection which will act on the heater only, stopping the heater and allowing the fans to continue on reaching set point.

- Water heated units shall have the option of an external solenoid valve. The solenoid valve shall be switched by the controller.

- Optional controllers shall be available which will provide automatic control with manual override.

- Optional BMS Interface shall be available if required. This shall give the BMS direct control of the fan speed selection. In the case of an electrically heated unit the BMS shall have control of the heat settings. In the case of water heated units with optional solenoid valve the BMS shall be capable of switching the solenoid valve. All interfacing to the BMS will be done using volt free contacts.

- The system is to be supplied by:

JS Air Curtains

Member of the Condair Group

Artex Avenue

Rustington

LITTLEHAMPTON

West Sussex

BN16 3LN

Tel: +44 (0) 1903 858 656 			Fax: +44 (0) 1903 850345

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com