# JS Air Curtains Smart Air Curtain Specification

- The Smart Air Curtain features a stylish, contemporary design for horizontal installation, with a self-supporting galvanised steel casing. The casing has rounded edges incorporating curved plastic side covers.

- The Smart casing is finished with a structural epoxy-polyester paint finish, offered in standard RAL 9016 (White), with other RAL classic colours available on request. Its smooth front panel can also be customised with logos, lighting, signage, or lettering to suit branding or design needs.

- As standard, the fans are ‘AC’ type, with double inlet centrifugal design, featuring low noise levels. They use an external rotor motor, offer five selectable speeds, and come equipped with built-in thermal protection. Two power options are available to accommodate various mounting heights and operating conditions.

EC (electronically commutated) fans with low energy requirements can be specially ordered, offering enhanced energy efficiency, lower operating costs, and sophisticated control options.

- The Smart unit shall measure 270mm high by 565mm deep and can be supplied in various lengths ranging from 1.0m to 3.0m in 0.5m increments.

- The unit is designed for exposed, horizontal mounting above doors utilising M8 threaded drop rods. Optional brackets may be specially ordered for overhead or wall mounting, including, wall ‘rail’ supports, suspension cables or Omega wall supports.

- The air inlet grille is hidden in the upper part of the unit making it an attractive air curtain for commercial entrances. Only routine cleaning or vacuuming is needed in normal conditions.

- The unit can be specified with various regulated heating options: ‘A’ type (low-energy air only, unheated or recirculating ambient air), ‘E’ type (electric element heating with three stages), or ‘P’ type (LPHW water coil).

- E’ type electric units shall operate on 400V/50Hz three-phase power, include power contactors and feature shielded elements, with three standard heating stages.

- ‘P’ type water heated units shall offer on/off or proportional heating control, with coil options for either 50°C, 60°C or 80°C flow. Automatic external solenoid valves and special coils for ‘low grade’ water shall also be available on request.

- The unit comes with anodised aluminium vanes shaped like air foils to minimise drag and noise.

- The Smart is equipped as standard with an ‘Advanced Pro’ digital controller, featuring a 2.8” backlit LCD status screen, capacitive touch buttons, a tamperproof screen lock, and a lacquered PCB for enhanced protection against moisture and dust. The package also includes a 7m, RJ11 control cable, door contact and a handheld infrared remote control.

- The controller features an integrated temperature sensor, with semi-automatic ECO mode for setpoint regulation, with manual override for temperature and fan speed adjustment. ECO Mode settings can be configured based on door status, including door delay (0 to 95 sec), maximum speed and heating (open and closed), maintenance/filter intervals (0 to 92 weeks), temperature boost mode, and additional related functions.

- The controller features ‘Plug & Play’, auto configuration with a backlit LCD showing temperature, fan speed, heating, door status, alarm/error and unit off. It also includes three digital inputs for BMS/timer enable/disable, heat enable/disable, fire alarm disable, with manual safety reset.

- The optional ‘Clever Pro’ controller includes all ‘Advanced Pro’ features, plus a 7-day timer, and Modbus RTU compatibility with BMS, for remote control.

- The Smart air curtain is produced to ISO 9001 standards, fully run tested for reliability, with traceable documentation for quality, is CE & UKCA certified and compliant with relevant regulations. BIM files can be provided upon request.

- The system is to be supplied by					www:	Smart Air Curtain

JS Air Curtains Limited

City Gates, 2-4 Southgate

Chichester

West Sussex 							Tel:	+44 (0)333 038 4240

PO19 8DJ	 							e-mail:	sales@jsaircurtains.com

United Kingdom							Website:	www.jsaircurtains.com