# JS Air Curtains Top, Air Curtain Specification

- The Top Air Curtain unit features an industrial yet decorative design for horizontal installation, with self-supporting galvanized steel casing.

- The Top casing is finished with a structural epoxy-polyester paint finish, offered as standard with RAL 9016 bottom cover and RAL 9006 front face. Other RAL classic colours, or a stainless steel finish, are available on request. The front face can also be customised with logos, lighting, signage, or lettering to suit branding or design needs.

- The unit is equipped with ‘AC’ tangential, cross-flow fans, powered by an external rotor motor and featuring low noise levels. They offer two selectable fan speeds and are equipped with built-in thermal protection.

- The Top unit shall measure 223mm high by 420mm deep and can be supplied in lengths of 1.0m, 1.5m, and 2.0m.

- The unit is designed for exposed, horizontal mounting above doors utilising M8 threaded drop rods. Optional brackets may be specially ordered for overhead or wall mounting, including, wall ‘rail’ supports and suspension cables.

- The air inlet grille is perforated, with filter function, to allow easy servicing, so only routine cleaning or vacuuming is needed in normal conditions.

- The unit can be specified with various regulated heating options: ‘A’ type (low-energy air only, unheated or recirculating ambient air), ‘E’ type (electric element heating with three stages), or ‘P’ type (LPHW water coil).

- E’ type electric units shall operate on 400V three-phase, or 230V power, include power contactors and feature shielded elements, with three standard heating stages.

- ‘P’ type water heated units offer either on/off, or proportional heating control, depending on valve type, with coil options for 60°C or 80°C flow. External solenoid valves shall also be available on request.

- The unit comes with anodised aluminium vanes shaped like air foils to minimise drag and noise.

- The Top is equipped as standard with an ‘Advanced Pro’ digital controller, featuring a 2.8” backlit LCD status screen, capacitive touch buttons, a tamperproof screen lock and a lacquered PCB for enhanced protection against moisture and dust. The package also includes a 7m, RJ11 control cable, door contact and a handheld infrared remote control.

- The Advanced Pro controller features an integrated temperature sensor, with semi-automatic ECO mode for setpoint regulation, with manual override for temperature and fan speed adjustment. ECO Mode settings can be configured based on door status, including door delay (0 to 95 sec), maximum speed and heating (open and closed), maintenance/filter intervals (0 to 92 weeks), temperature boost mode, and additional related functions.

- The controller features ‘Plug & Play’, auto configuration with a backlit LCD showing temperature, fan speed, heating, door status, alarm/error and unit off. It also includes three digital inputs for BMS/timer enable/disable, heat enable/disable, fire alarm disable, with manual safety reset.

- The optional ‘Clever Pro’ controller includes ‘Advance Pro’ features (excluding fire alarm input), plus a 7-day timer, and Modbus RTU compatibility with BMS, for remote control.

- The Top air curtain is produced to ISO 9001 standards, fully run tested for reliability, with traceable documentation for quality, CE & UKCA certified and compliant with relevant regulations. BIM files can be provided upon request.

- The system is to be supplied by:

JS Air Curtains Limited 						www:	Top Air Curtain

City Gates, 2-4 Southgate

Chichester

West Sussex								Tel:	+44 (0)333 038 4240

PO19 8DJ 								e-mail:	sales@jsaircurtains.com

United Kingdom 							Website:	www.jsaircurtains.com