# JS Air Curtains Zen Air Curtain Specification

- The Zen Air Curtain is designed in a refined, minimalist architectural style and features as standard front and rear fascia panels, constructed from anodised aluminium, with zinc-plated steel central structure in Black Forge RAL 9913 finish.

- The Zen facia panels offer custom finishes, including materials such as stainless steel, stone or leather, with graphics or logos, illuminated signage, or other specified decorative elements, such as clocks. The facia panels or central structure are also available in any RAL chart colour upon request.

- As standard, the Zen fans are ‘AC’ type, with double inlet centrifugal design, featuring low noise levels. They use an external rotor motor, offer five selectable speeds, and come equipped with built-in thermal protection. Two power options are available to accommodate various mounting heights and operating conditions.

- EC (electronically commutated) fans with low energy requirements can be specially ordered, offering enhanced energy efficiency, lower operating costs, and sophisticated control options.

- The Zen unit is designed with a height of 473mm and a depth of 291mm, and it can be supplied in various lengths ranging from 1.0m to 3.0m in 0.5m increments. Additionally, multiple units may be joined together by special order.

- The unit shall be suitable as standard for exposed, horizontal mounting above door, hung using M8 threaded drop rods. An optional base plate with floor fixing points shall be available, to allow vertical mounting to side of the doorway.

- Optional brackets may be supplied upon special request for either wall or floor installation. These include 'wall supports' or floor-mounted 'goalpost supports,' with the additional option of finishing in a designated RAL colour paint.

- The air inlet grille is perforated with filter function, to allow easy servicing, so only routine cleaning or vacuuming is needed in normal conditions.

- The unit can be specified with various regulated heating options: ‘A’ type (low-energy air only, unheated or recirculating ambient air), ‘E’ type (electric element heating with three stages), or ‘P’ type (LPHW water coil).

- E’ type electric units shall operate on 400V/50Hz three-phase power, include power contactors and feature shielded elements, with three standard heating stages.

- ‘P’ type water heated units shall offer on/off or proportional heating control, with two coil options for either 80°C or 60°C flow. Automatic external solenoid valves and special coils for ‘low grade’ water shall also be available on request.

- The unit comes with anodised aluminium vanes shaped like air foils to minimise drag and noise. Each vane can be adjusted from 0 to 15º from the vertical to control the direction of airflow.

- The Zen is equipped as standard with an ‘Advanced Pro’ digital controller, featuring a 2.8” backlit LCD status screen, capacitive touch buttons, a tamperproof screen lock, and a lacquered PCB for enhanced protection against moisture and dust. The package also includes a 7m, RJ11 control cable, door contact and a handheld infrared remote control.

- The controller features an integrated temperature sensor, with semi-automatic ECO mode for setpoint regulation, with manual override for temperature and fan speed adjustment. ECO Mode settings can be configured based on door status, including door delay (0 to 95 sec), maximum speed and heating (open and closed), maintenance/filter intervals (0 to 92 weeks), temperature boost mode, and additional related functions.

- The controller features ‘Plug & Play’, auto configuration with a backlit LCD showing temperature, fan speed, heating, door status, alarm/error and unit off. It also includes three digital inputs for BMS/timer enable/disable, heat enable/disable, fire alarm disable, with manual safety reset.

- The optional ‘Clever Pro’ controller includes all ‘Advance Pro’ features, plus a 7-day timer, and Modbus RTU compatibility with BMS, for remote control.

- The Rund air curtain is produced to ISO 9001 standards, fully run tested for reliability, with traceable documentation for quality, is CE & UKCA certified and compliant with relevant regulations. BIM files can be provided upon request.

- The system is to be supplied by					www:	Zen Air Curtain

JS Air Curtains Limited

City Gates, 2-4 Southgate

Chichester

West Sussex 							Tel:	+44 (0)333 038 4240

PO19 8DJ	 							e-mail:	sales@jsaircurtains.com

United Kingdom							Website:	www.jsaircurtains.com